## Slide 1
Field | Central Heating
Chapter | Regulations concerning the annual maintenance of installations
Subtitle | Discharge by natural draught

## Slide 2
1. Discharge of Combustion Products from Devices Type B by Natural draught
- The combustion products must be carried aboe the building. This requires energy that is either natural or mechanical.
- The natural energy originates from the difference in specific mass between the combustion products (warm gases) and the ambient air (cold air).
- When a quantity of air is heated, it expands, increasing its volume. However, the total mass remains the same, so that the mass per m³ becomes smaller.
- Warm air has a smaller specific mass than cold air.

## Slide 3
1. Discharge of Combustion Products from Devices Type B by Natural draught
- In a mixture of combustion products and ambient air, the hot gases, especially the combustion products, will rise.
- The warm combustion products rise in the exhaust duct to which the appliance's drain is connected.
We call this phenomenon “THERMAL DRAFT”
- It is as if the cold air pushes the warm combustion products up through the exhaust duct. The greater the temperature difference, the greater the force with which this happens.

## Slide 4
1.1 Thermal draught
- It is important that the thrust does not decrease too much before the combustion products have left the discharge channel at the end.
- The temperature of the combustion products in the exhaust duct must not drop to a value at which the driving effect disappears, and the velocity drops to zero

## Slide 5
1.1 Thermal Draught
- The most critical conditions are those when starting up the device.
- The exhaust duct is then relatively cold.
- The energy required to push the combustion products to the top of
the exhaust duct is maximum.
- When starting up an appliance, it is quite normal that there is a brief backflow of the combustion products to the place where the appliance is installed.
- A good exhaust duct will heat up quickly and provide sufficient thermal draft, which is referred to as an exhaust duct with low inertia.
- In addition, when the water vapor present in the combustion products cools down to below the dew point, condensation can occur in the exhaust duct with all the unpleasant consequences that entails.

## Slide 6
1.2 Checking the draught of a drain
- All connected appliances must operate at their rated power.
- The exhaust duct must be at the right temperature.
- The check itself can most easily be carried out at the draft diverter of the appliance. If the exhaust duct pulls well, fresh air will be sucked in (tertiary air).
- This can be quickly detected using a match or a cigarette or with a smoke
cartridge. Any recoil can be made visible with a mirror.
- The draft of the drain can also be measured with an anemometer or with a sensitive negative pressure gauge.

## Slide 7
1.3 Material requirements for connection and discharge ducts
- Before discussing the drain and connection duct requirements, we examine the suitable materials.
- The properties of combustion products—temperature, pressure, chemical composition, condensation, and soot—determine the choice of connection and exhaust duct for consumer appliances.

## Slide 8
1.3 Material requirements for connection and discharge ducts
- The standards NBN EN 1443 and NBN EN 1856-1 classify connecting and exhaust ducts by their resistance using different class designations.
- We distinguish, among other things:
- Temperature class
- Pressure class, negative pressure, positive pressure, high positive pressure
- Resistance to condensates
- Resistance class against corrosion
- Resistance to chimney fire
These classes offer the opportunity to make the right choice of material for the connection and exhaust duct to be used.

## Slide 9
1.4 Drain
(=channel that carries the combustion products outside the building)
- Each type B appliance is connected to an individual built-in or free-standing exhaust duct.
EXCEPT:
- Appliances with an atmospheric burner and total nominal power under 70 kW per space can share an exhaust duct if individual connections aren't feasible and regulations are followed.

## Slide 10
1.4.1 Construction of the drainage channel
- Chimney exhaust ducts must be independent of the building's structure and walls to prevent any adverse effects during normal operation. When designing the exhaust duct, the following points should be considered to limit noise pollution from the boiler:
- Noise levels in adjacent rooms must not exceed the maximum value
specified in NBN S 01-401.
- The location of the discharge outlet must comply with NBN S 01-401
requirements.
- When multiple ducts are combined, consider sound transmission between them
and choose rain protection to avoid sound reflection. Individual protection for
each duct is recommended.

## Slide 11
1.4.2 Design of the built-in exhaust duct
When designing a built-in exhaust duct, we must take the following points into account:
- Passage of the discharge channel
- Tightness of the drainage channel
- Followed path of the drainage canal
- Outlet of the drainage channel
- Rain protection
- Static discharge hood on the discharge duct
- Insulation of the exhaust duct
- Cleanliness of the drain
- Collection collector
- Water drainage for the drainage channel

## Slide 12
1.4.3 Special provisions for the design of a separate drainage channel
Before tubing, clean the drain channel thoroughly. If the exhaust duct is damp, leave an air gap between the tubing and the duct wall. If the duct is dry, fill the space with non-compressible material like perlite; avoid using compressible or hygroscopic materials. Ensure the pipe passage allows proper discharge of combustion products.
1.4.4 Special provisions for tubing an existing drain
When constructing a separate drainage channel, we must take the following special provisions into account:
- Confirmation
- Protection of the surrounding materials
- Line-up
- Thermal insulation

## Slide 13
1.5 Checking and Cleaning
- Flue gas discharge ducts from central heating systems must be checked and cleaned every two years. Follow these steps:
- Clean the ducts
- Check the ducts
- Measure and adjust the chimney draft

## Slide 14
1.6 Connection Channel
(=Duct connecting the appliance's exhaust stub or draft diverter to the combustion product duct)
1.6.1 Design of the connecting channel
For the implementation we must take the following points into account:
- The method of joining the pipes
- Used materials
- Use of flexible metal pipes subject to certain conditions
- Thermal insulation of the connection duct
- Protection of the surrounding materials
- Passage of the connecting channel
- Draft stabilizer valve
- Measuring opening

## Slide 15
1.6.2 Connection to the exhaust duct
- The connecting duct should be as short as possible, never slope downward, and, if longer than 0.50 m, slope upward toward the discharge duct.
- It should minimize resistance and avoid direction changes; if necessary, use curved bends.
- To prevent contaminants, a metal channel should extend 20 mm above and 5 mm below the masonry duct.
- Only the original draft diverter from the appliance is allowed.